## Estimated Costs Summary
SJC Water System Upgrade
PLC Hardware | 164400
PLC - Remote IO | 20000
UPS | 104000
SD-WAN network of sites to connect PLC, and other devices, to AWS, and to Ignition | 78755.6
Cabinets | 104462.5
Misc. Devices Required at site | 143200
Misc Instruments and Devices | 32000
Software | 37950
| 684768.1 | HW and SW Total
Software Labor | 692000
Misc Labor | 696000
| 1388000 | Labor Total
Annual Subscription Costs | 27000 | Per Year

## Estimated BOM and Costs Details
PLC Hardware
From Rexel
Micro 850E | 660
OW4I | 105 | For Drive Enable and Direction | [8 empty] | Micro 850E | 660
Memory | 280 | [9 empty] | OW4I | 105 | For Drive Enable and Direction
Power Supply | 75 | [9 empty] | Memory | 280
IF4 | 331 | [9 empty] | Power Supply | 75
OF4 | 331 | TBD | [8 empty] | IF4 | 331
End Cap | 23 | [9 empty] | OF4 | 331
ModBus Module |  | TBD | [8 empty] | End Cap | 23
| 1805 | Per Site
| 80 | Sites | [9 empty] | 1805
| 144400 | Total
PLC Dev SW | 475 | one Time
[11 empty] | PLC Dev SW | 475 | one Time
Remote IO | 1000 | add for some sites
| 20 | Sites | [8 empty] | Remote IO | 600
| 20000 | Total
144400
20000
164400
UPS
|  |  |  | 10 | A |  |  | 5 | A
|  |  |  | 120 | VA |  |  | 120 | VA
|  |  |  | 1200 | VA |  |  | 600 | VA
| UPS @ 60 minutes |  |  | 0.9 | PF |  |  | 0.9 | PF
| 5 amps, 5 Amp-Hours |  |  | 1080 | Watts |  |  | 540 | Watts
| 10 Amps, 10 Amp-Hours |  |  | 0.8 | Double-Conversion.. 0.8 efficiency |  |  | 0.8 | Double-Conversion.. 0.8 efficiency | for PureSine Wave Output
|  |  |  | 864 | Actual Watts |  |  | 432 | Actual Watts
|  |  |  | 120 | Volts |  |  | 120 | Volts
|  |  |  | 7.2 | Actual Amps |  |  | 3.6 | Actual Amps
Phoenix-Contact
|  | 1 KW UPS Controler AC-AC |  | 550 |  | QUINT4-UPS/1AC/1AC/1KVA - Uninterruptible power supply
|  | Batteries x 1, 12A-Hr |  | 450
|  | Labor |  | 300
|  |  |  | 1300 | Per Site
|  | extra batts, up to 192 A-Hrs |  | 80 | Sites
104000
Pro-Soft
SD-WAN network of sites to connect PLC, and other devices, to AWS, and to Ignition

|  |  | Quantity | Product Number | Description | LIST $ | $ Totals |  | Annual Costs
|  |  | Optional | RLX2-IHNF-A | 802.11abgn Fast Industrial Hotspot, includes 2dBi stub antenna, FCC | 1739
|  |  | 3 | PLX35-NB2 | Remote Access Network Bridge | 739 | 2217 |  |  | For Desktop connections
|  |  | 1 | PSC-PDN-ACT | PDN Account Activation Fee | 659 | 659
|  |  | 80 | PSC-PDN-SITE-1Y | PDN Subscription for 1 year for each site | 235 | na |  | 18800
|  |  | 80 | ICX35-HWC-A | Industrial Cellular Gateway - CDMA/EVDO/GSM/LTE Americas | 859 | 68720 |  |  | For site connections
71596
[6 empty] | Tax @ 10% | 7159.6
78755.6
| Cabinets |  | QTY | Item | Cost per Item | Total
| by Saginaw |  | 75 | 24hx24wx12d | 450 | 33750
| 24hx24w |  | 80 | 24hx24wx8d | 450 | 36000
|  |  | 5 | 24hx24wx16d | 500 | 2500 |  |  | Deep cabinets for inner door and/or HMI, and/or manual controls
|  |  | 160 | Sub-panels | 75 | 12000
|  |  | 5 | Inner-door | 115 | 575
|  |  | 80 | Lock and Key | 10 | 800
|  |  | 5 | door kit | 50 | 250
[5 empty] | Sub-Total | 85875
[5 empty] | Tax @ 10% | 8587.5
[5 empty] | Delivery | 10000 | ? |  | Need warehouse address for quote
[5 empty] | Total | 104462.5
| Misc. Devices Required at site | Supplier
|  |  | Costs | Est Required Per site | Cost Per Site
| Circuit Breakers, 2P-20Amp | Eaton
| Power Supply 120/24 | Phoenix-Contact | 55 | 4 | 220
| Motor Current Transformer w/AO | ? | 720 | 1 | 720 | TRIO3-PS/1AC/24DC/20/8C/IOL - Power supply unit
| Cellular Antennae and Cables | ? | 150 | 1 | 150 | Square D
| Misc cabinet hardware |  | 300 | 1 | 300
| Ethernet Sw 8 port | Phoenix-Contact | 200 | 1 | 200
|  |  | 200 | 1 | 200
0
0
0
0
0
[5 empty] | 1790 | Per Site
[5 empty] | 80 | Sites
143200
Misc Instruments and Devices
|  | HACH SC4500 |  | 4000 | 1 | 4000
|  | Cellular SIM config |  |  |  | 8000 | ?
|  | Drives |  |  |  | 0 | ?
|  | Soft-Start |  |  |  | 0 | ?
|  | Local HMI |  | 2000 | 10 | 20000 | ?
0
32000
Software
One-Time Costs
|  | Ignition | See quote |  |  | 37000
|  | PLC SW, CCW Pro |  | 475 | 2 | 950
|  | PLC SW, Studio |  |  |  | 5000
37950
Software Labor
|  |  | $/Hr | hours | sites
|  | AWS Configuration | 100 | 40 | 1 | 4000
|  | Ignition Configuration | 100 | 40 | 80 | 320000
|  | Pro-Soft SD-WAN configuration | 100 | 1 | 80 | 8000
|  | PLC Configuration | 100 | 40 | 80 | 320000
|  | Local HMI | 100 | 20 | 20 | 40000
0
692000
Misc Labor
| Install and Wiring |  | 100 | 40 | 80 | 320000
| Hotel, M & IE |  | 300 | 5 | 80 | 120000
| Cabinet Pre-Fab Off-site Labor |  | 100 | 16 | 160 | 256000
696000
Annual Subscription Costs
|  | Pro-Soft |  |  |  | 20000
|  | T-Mobile |  |  |  | 5000 | ?
|  | AWS |  |  |  | 2000 | ?
27000

## Device Interface
Device Interface
Device / Instrument | Website Link to Device info / Manual | Part # / Order Info | Available Protocols for PLC: Eth-IP, Modbus RTU, Modbus TCP/IP
Clorine Monitors, ATIs - Q46H | https://www.analyticaltechnology.com/us/ | Model Q46H/62-63 A-B-C-D-E-F-G | 3 - Modbus RTU,4 - Ethernet IP,5 - Modbus TCP/IP | Call ATI to Verify Power and Server/Client protocol
HACH SC4500 | https://www.hach.com/p-sc4500-controller-with-prognosys-and-lan-ma-analog/LXV525.99E1B561 |  | Profibus DPV1 module Modbus TCP Profinet IO module Ethernet IP module
Primex 3000 XC |  |  | Modbus RTU
Yaskawa Drives IQ 1000 Controller
Badger Meter M2000 HART | https://www.badgermeter.com/products/meters/electromagnetic-flow-meters/m2000-electromagnetic-flow-meter/#SubNavAnchor__Specifications |  | Modbus TCP-IP
Primex VPAC 6 | https://primexcontrols.wpenginepowered.com/wp-content/uploads/2018/06/Manual-7.pdf |  | Modbus TCP-IP
McCrometer F101 flowmeter | https://www.mccrometer.com/asset-get.download.jsa?id=52003822500
Samsara - IG21 |  |  | As Client, use Modbus RTU, As Server, use Eth-IP
Samsara - IG41 |  |  | As Client, use Modbus RTU, As Server, use Eth-IP
Submersible LIT | https://www.grainger.com/category/test-instruments/pressure-vacuum-measurement/submersible-level-transmitters?sst=4&ts_optout=true&searchQuery=Mercoid&categoryIndex=5

## SOW Per Site
Assume SJC will upgrade and re-calibrate instruments
|  |  |  | PLC |  | Pump Controllers | [9 empty] | New UPS Panel | New PLC+Cellular Panel, add to ALL sites.
Site Number | Location | Site Category | Site Type & Number of Pumps | Existing PLCs =========== Add new UPS and PLC panel. See appendix B. ========== A. Replace Micro 1100 and PICO, with Micro 850. B. Upgrade Compact PLC C. Replace Micro 1100 with Micro 850 D. Add Eth/IP comms to New PLC Panel. ========= | Non-Existant PLC. =========== Add new UPS and PLC panel. See appendix B. ========== Re-terminate field status and controls to New PLC. ========== Create local and SCADA HOA. | Existing Pump Controllers and VFD =========== Add Modbus RTU or Modbus IP, to New PLC Panel. =========== R/W tags per SJC =========== Add Lead-Lag controls to SCADA ========== Create local and SCADA HOA ========== | Non-Existing Pump Controllers ======== ?? | Existing Samsara All Samasara: Add Eth-IP cable and tags to new PLC panel and to SCADA. Keep Samsara system live and in parallel with new Scada until SJC approval to remove. Samsara tags should be pre-programmed within new PLC panel and in Scada before device removal. Old and new connection methods are to be pre-programmed within new PLC as separate sub-routines. A software sub-routine switch shall be programmed. =========== +++++++++++ At SJC approval, remove Samsara and connect existing Samsara IO to new PLC. Three scenarios: 1. IO are connected directly to Samsara. >> a. At removal, Replace Samsara with AB Micro 850. >>b. Add Eth-IP cable and tags to new PLC Panel. >>c. Initiate PLC software switch. 2. IO to existing PLC via Modbus RTU. >> At removal, Use Eth-IP from existing PLC to new PLC. Initiate PLC software switch. 3. IO to existing VFD via Modbus TCP/IP. >> At removal, connect Modbus TCP/IP cable to VFD from new PLC. Re-address IP as required. | Existing Special Instruments ========= Add Modbus RTU or Modbus IP, to New PLC Panel. =========== R/W tags per SJC =========== See Excel Sheet "Device Interface" | Add Panel Disconnect to existing motor control panel per NEC. | Existing HOA for Pressure Switch controlled pumps - Modify / re-wire to standard See Appendix B / HOA. =========== A. For Pressure Switch controlled pumps, two devices determine control operation - A 4-20mA Pressure Transducer, and a Dry Contact Pressure Switch. Existing hardwired control circuit includes the P.S. in series with a HOA. 1. With new control relay with 4 N.O. contacts, duplicate P.S. status. See Appendix B / Sensor Duplication. 2. Modify wiring of existing HOA to include CR-PressSw relay contact, a Key-Switch, and a PLC Digital Output - as shown in Appendix B / HOA. ============ B. If non-existant, add Time-Delay-OFF Timer within existing Motor Control Circuit to prevent re-start within 15 minutes. Add N.O. AUX contact to existing Motor Contactor. Add power and wiring from this N.O. to a new Time-Delay-Off. Use the N.C. contct of this TDO in series with the Motor Control Circuit. ============= C. If non-existant, add N.O. AUX contact to existing Motor Contactor. Add PLC(+) power and wiring from this N.O. to a new PLC Dig Input. ============= D. If non-existant, add one N.C. and one N.O. Thermal O.L. contact to existing Motor Contactor. Re-wire Motor Control Circuit to include the N.C. Add PLC(+) power and wiring from the N.O. to a new PLC Dig Input. ============= E. If non-existant, add E-Stop with one N.C. and one N.O. contact. Re-wire Motor Control Circuit to include the N.C. Add PLC(+) power and wiring from the N.O. to a new PLC Dig Input. | Existing HOA for Non-VFD =========== Modify existing physical HOA for each pump control. Auto Mode, use field devices/sensors. Hand Mode, use spring-return or timed hand switch. =========== Add or modify wiring to starter / controller =========== Add status and control to SCADA. | Existing HOA Add Reverse ========= Add Pump Reverse control wiring and hardware, ( spring-return handswitch and control relay ). Add FWD/REV wiring to starter or VFD. Modify/Replace Motor Contactor, Soft-Starter for FWD and REV Add status and control to SCADA. | Existing Local Panel HMI ========= Replace AB HMI with EZ-Automation 12" HMI, no-cut-out model. ========= | Existing Site Generator ======= Info Only | Add New UPS panel with one 12 Amp-Hr Batt See Appendix B / UPS 24 x 24 x 8 ======== If non-existant, to power this UPS, add 480/120V, 2.4 KVA transformer with 30A Disc. Sw. wired from eisting 3 phase power circuit. ======== Add status wiring to New PLC. Add to SCADA. ========== For outdoor sites, add temperature controlled 4 in fan ( top/outbound) and 4 in vent (bottom) | Control Panel Space Available / Notes... See Appendix B 24 x 24 x Depth(D) D=12" w/o additions D=16" w/HMI or HOA or inner door. ========== For outdoor sites, add temperature controlled 4 in fan ( top/outbound) and 4 in vent (bottom) to new PLC Panel. | Add 15 PSi Submerged Level Transducer and wire to PLC Analog Input Add to SCADA. See 'Device Interface' | Add Water pressure sensor - transducer, and wire to PLC Analog Input Add to SCADA. See 'Device Interface' | Motor CT Required Add CT, Analog Input, wiring, PLC and SCADA programming. See 'Device Interface' ========= Hi Amp Alarm Motor Starts Motor Run-Time Amp history / Trend | Add status and wiring from NEW and Existing UPS panel. All Sites | Add Ethernet to Remote IO for existing PLC Panels Add Ethernet to existing Instruments, Pump Controllers, and/or VFD Refer to Columns E thru M | Add Cellular antenae and cable from each panel. All Sites | Control Narrative | Priority 1 High 5 low
|  |  | Storm-1Pump, Storm-2Pump, Well-1Pump, Well-2Pump Booster-1Pump, Booster-2Pump, Water Treatment, Wastewater-2Pump, Wastewater-3Pump | A,B,C, D | Yes=Non-Existant PLC | Primex3000XC-MB-RTU PrimexVPAC6-MB-IP Yaskawa IQ-Pump1000 MB-RTU Device & Protocol |  | Samsara IG21- Temporary ETH-IP to New PLC Panel Samsara IG41 - Temporary ETH-IP to New PLC Panel | Device & Protocol | Yes / No |  |  |  | 1. Existing - Needs Upgrade 2. Non-Existing, Add New 3. None required | Yes / No | All Sites | All Sites |  |  | One CT per Motor
1 | Flag City County Service Area 31 Wastewater Treatment Facility | Wastewater Treatment | PLC Upgrade Wastwater-3Pump | B, D |  |  |  | IG41 I/O from PLC | Badger Flow Meter Modbus TCP-IP | NO |  | manual mode for duty pump | reverse CR for Duty pump only | YES 1 | YES |  |  | NO | No | 3 |  |  |  | See special sites PLC upgrade amendment | 1
2 | Flag City Csa #13 Well #1 |  | Well-1pump |  | YES |  |  |  |  | NO | pressure switch control |  |  | NO-3 | NO |  | No room in panel, room in building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specif range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low water pressure, high electrical current | 1
3 | Flag City CSA #13 Storm Site | Storm Water | Storm-2pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | no room in panel, outdoor site would need concrete footing H frame with secure enclosure | Yes | NO | 2 |  |  |  | monitor sump level to call and stop alternating pump motors, provide a Low-Low to stop all pump operation and provide alarm, Low Level to stop operating pump, high Level to call pump, high-high to call both pumps and alarm | 4
4 | Flag City County Service Area 31 Well #2 | Well | Well-1pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | H frame would need to be intalled in a secure cage next to the secure cage of the control cabinet to avoid vandalism | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specif range) to provide I/O to call and stop well motor. monitor electrical current and alarm | 1
5 | Flag City County Service Area 31 Well #3 (Truck Stop) | Well | PLC upgrade Nitrate treatment plant | A, D |  |  |  |  | Hach SC4500 Modbus TCP-IP | NO |  |  |  | YES-2 | YES |  |  | NO | NO | 1 |  |  |  | See special sites PLC upgrade amendment create a panic mode fault disable operations PLC (incorperate an Alarm Reset button to reset PLC) | 1
6 | Thornton County Service Area 12 Well #2 | Well | PLC upgrade Well-1Pump Booster-2Pump | B, D |  |  |  | IG21 I/O From PLC |  | NO | pressure switch control requested | see amendment for more information |  | YES-1 | YES |  | Possibly room in the panel once removing the auto dialer. see pictures otherwise the only other available space is outside the building on the western exposure | NO | NO | 4 |  |  |  | See special sites PLC upgrade amendment | 1
7 | Thornton County Service Area 12 Booster Station | Booster Station | PLC Upgrade Booster-4Pump | B, D Upgrade two Compact PLCs |  |  |  |  | ATI Chlorine Anylizer Modbus TCP-IP | NO | pressure switch control requested | see amendment for more information |  | yes-2 | YES |  | POssible room inside the panel after plc upgrade otherwise H frame would be best on eastern exposure of cabineet | NO | NO | 4 |  |  |  | See special sites PLC upgrade amendment | 1
8 | Thornton County Service Area 12 Well #1 | Well | Well-1Pump Booster-1Pump |  | YES |  |  |  | Replace TESCO LIQUITRONICS II, with PLC IO and logic | NO | pressure switch control requested |  |  | NO-3 | NO |  | more details TBD | NO | YES | 3 |  |  |  | Monitor Wet well level with pre-defined levels to call and stop Well and blower motors, monitor System water pressure with user defined setpoints (within Specified range) to call and stop booster pump motor monitor electrical current and alarm, alarm for wet well high and low alarm setpoints | 1
9 | Mokelumne Acres Maintenance District Well #9 | Well | Well-1Pump |  | YES |  |  | IG41 I/O without PLC |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | Room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm monitor ATS position alarm for generator fail to run. | 1
10 | Mokelumne Acres Maintenance District Well #3 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | The Generator motor Inside the building makes for cramped quarters. ther is room on the northern exposure outsid ethe building between the PGE electriv and gas meteres, otherwise the easten or southern exposures are better suited for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low water pressre, high electrical current | 3
11 | Mokelumne Acres Maintenance District Well #7 | Well | Well-1Pump Emergency Run |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | There is room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure alarm for runtime (well is emergency use only notice to public must be issued within 24hrs upon runtime | 1
12 | Mokelumne Acres Maintenance District Well #8 | Well | Well-1Pump |  | YES |  |  |  | ATI Chlorine Anylizer Modbus TCP-IP | NO | pressure switch control requested |  |  | NO | YES |  | There is room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm. Monitor Cl2 sensor to provide alert for low level residual and alarm for high level redsduial | 1
13 | Mokelumne Acres Maintenance District Well #6 | Well | Well-1Pump VFD |  | YES |  |  |  | ATI Chlorine Anylizer Modbus TCP-IP | NO |  |  |  | NO-3 | NO |  | The Well head and motor Take up substantial space insid the building, There is space available between the Control cabinet and door inside the building, otherwise only the southern and wester exposures are availible outside the building | NO | YES | 0 |  |  |  | Monitor, and read modbus tags from yaskawa drive, monitor Cl2 sensor, alert low residial, alarm high residual. provide additional water pressure sensor to be monitored by PLC, monitoring pressure from PLC and and Modbus tag, alarms for high and low water pressure (the Yaskawa iQpump will stop reporting during a power outage to continue to monitor water pressure during outage conditions an additional pressure switch is neccisary to be connected to the PLC under UPS emergency power) | 1
14 | Fairway Estates County Service Area Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | there is room inside the building at the north eastern exposure otherwise space is available ouside the bui;ding on the eastern and western exposures | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. monitor ATS position alarm for generator fail to run. | 1
15 | Fairway Estates County Service Area Well #2 | Well | Well-1Pump VFD |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Outdoor site, there is space available adjacent to the control cabinet | NO | YES | 1 |  |  |  | monitor and read modbus tags from Yaskawa drive, provide additional Water pressure sensor to monitored by PLC monitoring pressure from PLC and and Modbus tag, alarm for low and high water pressure (the Yaskawa iQpump will stop reporting during a power outage to continue to monitor water pressure during outage conditions an additional pressure switch is neccisary to be connected to the PLC under UPS emergency power) | 1
16 | Acampo Maintenance District Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
17 | Acampo Maintenance District Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | there is room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. monitor ATS position alarm for generator fail to run. | 2
18 | San Joaquin Water Works #2 Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | room inside building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specif range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. monitor ATS position alarm for generator fail to run. | 1
19 | San Joaquin Water Works #2 Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | outdoor site, room adjacent to control cabinet for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specif range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. | 2
20 | Clements County Service Area 43 Well #1 | Well | Well-1Pump |  | YES |  |  | IG41 I/O without PLC |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | room inside building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specif range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. monitor ATS position alarm for generator fail to run. | 1
21 | Clements County Service Area Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | room inside building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specif range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. monitor ATS position alarm for generator fail to run. | 1
22 | Morada Estates North County Service Area 46 Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | No room in panel, room in building for H frame | NO | YES | 1 |  |  |  | monitor water pressure, water flow pulse output meter, utilizing user defined setpoints (within spaecified range) provide I/O to call and stop well pump motor. monitor e;ectrical current of motor and call alarm for high currunt, alarm for low and high water pressure | 1
23 | Morada Estates North County Service Area 46 Well #3 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | No room in panel, room in building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. monitor ATS position alarm for generator fail to run. | 1
24 | Morada Estates North County Service Area 46 Well #1 | Well | Well-1Pump Emergency Run |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | No room in panel, room in building for H frame | NO | YES | 1 |  |  |  | monitor water pressure alarm for runtime (well is emergency use only notice to public must be issued within 24hrs upon runtime provide user defined setpoints to run and stop well pump motor monitor ATS position and alarm for generator runtime failure | 1
25 | Wilkinson Manor Maintenance District Well #3 | Well | Well-1Pump VFD |  | YES |  |  | IG41 I/O fromTCP-IP I/O(Yaskawa VFD) I/O without PLC | ATI Chlorine Anylizer Modbus TCP-IP | YES |  |  |  | NO-3 | YES |  | there is panel space, it is shared wiht high voltage electrical, there is space for an h frame, but it is cramped in the building, Directly outside the building is cramped also. see site photos | NO | YES | 1 |  |  |  | monitor and read modbus tags from Yaskawa drive provide additional Water pressure sensor to monitored by PLC monitoring pressure from PLC and and Modbus tag monitor position of ATS alarm for generator runtime failure, Alarm Yaskawa drive alarms (the Yaskawa iQpump will stop reporting during a power outage to continue to monitor water pressure during outage conditions an additional pressure switch is neccisary to be connected to the PLC under UPS emergency power) | 1
26 | Wilkinson Manor Maintenance District Well #2 | Well | Well-1Pump Emegency Run |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is no room inside the panel, there is a shack onsite with room for an H frame, there is also a concrete pad with room to install H frame | NO | YES | 0 |  |  |  | monitor water pressure alarm for runtime (well is emergency use only notice to public must be issued within 24hrs upon runtime provide user defined setpoints to run and stop well pump motor | 1
27 | Morada Estates Maintenance District Well #1 | Well | Well-1Pump Offline |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is no room in the panel, there is rooom inside the building for h frame | NO | YES | 1 |  |  |  | Well is offline. the equipment provided for this site may be used elsewhere or as a redundant point of system water pressure as the water from well 2 is pumped directly to this sites pressure vessel | 5
28 | Morada Estates Maintenance District Well #2 | Well | Well-1Pump VFD |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is room inside the building for h frame | NO | YES | 0 |  |  |  | monitor and read modbus tags from Yaskawa drive, provide additional Water pressure sensor to monitored by PLC, monitoring pressure from PLC and and Modbus tag, alarm for low and high water pressure | 1
29 | Morada Manor Maintenance District Well #1 | Well | Well-1Pump VFD |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is an abandoned wellhead in the buildinlg making for close quarters, i think the installoer may want to install footings outside to install H frame | NO | YES | 0 |  |  |  | monitor and read modbus tags from Yaskawa drive, provide additional Water pressure sensor to monitored by PLC, alarm for low and high water pressure(the Yaskawa iQpump will stop reporting during a power outage to continue to monitor water pressure during outage conditions an additional pressure switch is neccisary to be connected to the PLC under UPS emergency power) | 1
30 | Almond Park Maintenance District Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
31 | Morada Acres Maintenance District Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | the active wellhead is inside the builing making for tight quarters, there is room for h frame outside the building | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
32 | Gayla Manor Maintenance District Well #1 | Well | Well-1Pump VFD |  | YES |  |  | IG41 I/O fromTCP-IP I/O(Yaskawa VFD) I/O without PLC |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | the best space in the building for an H frame is currently occupied by my lame samsara panel, i will move it | NO | YES | 0 |  |  |  | monitor and read modbus tags from Yaskawa drive, provide additional Water pressure sensor to monitored by PLC, monitoring pressure from PLC and and Modbus tag, alarm for low and high water pressure, alarm Yaskawa drive alarms (the Yaskawa iQpump will stop reporting during a power outage to continue to monitor water pressure during outage conditions an additional pressure switch is neccisary to be connected to the PLC under UPS emergency power) | 1
33 | Shaded Terrace Maintenance District Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is no room in the panel, there is room next to it for footings and a H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
34 | Walnut Acres Maintenance Distrcit water and Storm water facility | Water & Storm Water | Well-2Pump Storm - 1 Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | there is room inside the building for H frame | NO | YES | 3 |  |  |  | monitor system water pressured, using user defined setpoints (within specified range) to provide I/O to call and stop well motors.provide I/O for Lead - Lag positions wells ato be alternated at user defineed intervals. monitor electrical current of 2 well motors and 1 storm pump motor. monitor level of storm sump and provide I/O to pumpdown storm sump at user defined intervals. alarm for low and high water pressure, high motor currents, high level storm sump | 1
35 | Waterloo 99 County Service Area 15 Wastewater treastment | Wastewater Treatment | Wastewater Treatment Plant - 2 Pump |  | YES |  |  |  |  | NO |  |  | 2 reverse pumps | YES-2 | NO |  | See Pictures there is some space available on the wall inside the building if the flow meter output device is incorperated onto cabintet also the cotrol cabinet can be upgraded to incorperate equipment. Otherwise space is available outside the building on the western exposure under the awning, inside the building the plant air blowers create a +20 degree temerature swing. | YES | NO | 2 |  |  |  | monitor sanitary sewer sump level to provide I/O for pumpdown cycle. alow for user defined timed motor run intervals (within specified range) to not surcharge the sewer treatment plant, and alow for varying heights of pumpdown to alow for reduction of "Grease Ring," Sewer pumps must alternate.utilize Low-Low Shutdown and alarm, Low level stop, High level call, and High High Level alarm and call of both sewer pumps. Provide I/O for reverse run of sewer pumps. Monitor and Alarm electrical current of sewer pumps monitor level of Sewer Plant digester tank to alert at user defined level for decant protocol. | 1
36 | Lincoln Village Maintenance District Wastewater | Wastewater Treatment | Wastewater-2 Pump VPAC 6 |  | YES |  | Primex VPAC 6 Modbus TCP/IP INSTALLED BY SJC |  |  | NO |  |  | 2 reverse pumps | NO-3 | NO |  | See site photos. There is no room on the floor to mount H frame without moving sump washdown equipment, there is space on the wall to mount cabinet. =================== | YES | YES | 2 |  |  |  | monitor sanitary sewer sump level to provide I/O for pumpdown cycle.alow for varying heights of pumpdown to alow for reduction of "Grease Ring," Sewer pumps must alternate.utilize Low-Low Shutdown and alarm, Low level stop, High level call, and High High Level alarm and call of both sewer pumps. Provide I/O for reverse run of sewer pumps | 1
37 | Pacific Gardens Lift Station | Lift Station | Wastewater - 2 Pump VPAC 6 |  | YES | Primex VPAC 6 |  |  |  | NO |  |  | repleace current reverse switches with reverse CRs, Add status of each to PLC. | NO-3 | YES |  | there is some room for frame, across the room from controls cabinet. see photos. there is room on the the northern exposure outside the building | YES | No | 2, replace existing CTs |  |  |  | monitor and read tags of Primex control panel, provide I/O for reverse run sewer pumps operation monitor and alarm sewer pump electrical current, alarm primex alarms | 1
38 | Hospital Lift Station | Lift Station | Wastewater - 3 pump |  | YES | Primex-3000XC Modbus RTU |  | IG41 I/O from PLC, I/O from RS485 serial Modbus RTU (Primex PC3000-XC) | Badger M2000 Flowmeter Modbus TCP-IP | NO |  |  |  | NO-3 | YES |  | there is room for H frame adjacent to control panel, must incorperate or move flow meter output devices. Government buildings strongly considering a major upgrade to the station (new pumps, controls, and equipment,) the timeline is after the SCADA projects completion. the SCADA equiment will be incorperated into the new cabinet when installed. | NO | No | 4 |  |  |  | monitor and read tags of Primex pump controller monitor and read modbus tags of badger flow meter controllers (Currently I am waiting for the TCP-IP daughterboards for the badger meter cotrollers, flow is monitored by 4-20 output from the meter controller sent to the AI card of a micro 820, IP to Samsara) monitor motor electrical current, alarm high sump, alarm primex alarms monitor Exhaust fan motor current for operation | 1
39 | Santos Ranch County Service Area 35 Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | Well is Currently under reconstruction. work is expected to be completed April '24 wellhead is located inside building making for tight spaces. itherwise space is avalable on northern and eastern exposures ouside the building for H frame | NO | No | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
40 | Santos Ranch County Service Area 35 Well #2 | Well | Well-1Pump |  | YES |  |  | IG41 I/O without PLC |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | thered is room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low pressure, high current. monitor ATS position alarm for generator fail to run. | 2
41 | Corral Hollow Maintenance District Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | there is no room inside the panel, there is roominside the building | NO | YES | 1 |  |  |  | monitor and read modbus tags from Yaskawa drive, provide additional Water pressure sensor to monitored by PLC, alarm for low and high water pressure Alarm Yaskawa drive alarms | 2
42 | Corral Hollow Maintenance District Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | there is no room in the panel, room availible inside and outside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
43 | Fair Oaks Well #4 | Well | PLC upgrade Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | the control section of the cabiet is available as part of the PLC upgrade | NO | YES | 1 |  |  |  | See special sites PLC upgrade amendment | 2
44 | Fair Oaks Well #3 | Well | Well-1Pump VFD |  | YES |  |  | IG41 I/O fromTCP-IP I/O(Yaskawa VFD) I/O without PLC | ATI Chlorine Anylizer Modbus TCP-IP | NO |  |  |  | NO-3 | YES |  | The Control section of the cabinet is available | NO | NO | 1 |  |  |  | monitor and read modbus tags from Yaskawa drive, provide additional Water pressure sensor to monitored by PLC, monitoring pressure from PLC and and Modbus tag, monitor position of ATS alarm for generator runtime failure, Alarm Yaskawa drive alarms (the Yaskawa iQpump will stop reporting during a power outage to continue to monitor water pressure during outage conditions an additional pressure switch is neccisary to be connected to the PLC under UPS emergency power) | 1
45 | Fair Oaks Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | there is room inside the building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 2
46 | Costello Sewer Treatment Plant | Wastewater Treatment | WWTP-Tag read Write / Wastewater_2Pump 3000XC | C,D |  |  | Primex-3000XC Modbus RTU TO BE INSTALLED BY SJC | IG21 I/O From PLC |  | NO |  |  |  | No, existing, do not upgrade | YES |  | there is some space available inside the control cabinet where the communication equipment (samsara / DSL modem) reside otherwise space is available for H frame | NO | NO | 0 |  |  |  | monitor and read tags from plant AB MicroLogix PLC. Adjacent to sewer plant, monitor sanitary sewer sump level to provide I/O for pumpdown cycle.alow for varying heights of pumpdown to alow for reduction of "Grease Ring," Sewer pumps must alternate.utilize Low-Low Shutdown and alarm, Low level stop, High level call, and High High Level alarm and call of both sewer pumps. Provide I/O for reverse run of sewer pumps. Alarm for High Level sump, alarm AB Micro logix alarms | 1
47 | Zephyr Lift Station | Lift Station | Wastewater-2 Pump 3000XC |  | YES |  |  | IG41 I/O without PLC |  | NO |  |  | Reverse CR Requested | NO-3 | YES |  | outdoor site, there is space available ajacent to control cabine for H frame | NO | NO | 2 |  |  |  | monitor and read tags of Primex control panel, provide I/O for reverse run sewer pumps operation monitor and alarm sewer pump electrical current, alarm primex alarms, monitor ATS and provide alarm for generator runtime failure | 1
48 | Linney Wastewater Treatment | Wastewater Treatment | WWTP-Tag read Write | B, D |  |  |  | IG21 I/O From PLC |  | NO |  |  |  | NO, exinsting, Do not Upgrade | YES |  | there is some space available inside the control cabinet where the communication equipment (samsara / DSL modem) reside otherwise space is available for H frame | NO | NO | 0 |  |  |  | monitor and read tags from plant AB MicroLogix PLC, alarm AB Micro logix alarms | 1
49 | Par County Estates County Service Area 16 Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | Outdoor site pending PGE inspection for internal improvements to high voltage electrical equipment | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 2
50 | Par County Estates County Service Area 16 Well #3 | Well | Well-2Pump |  | YES |  |  | IG41 I/O without PLC |  | NO | pressure switch control requested |  |  | NO-3 | YES |  | room in building for H frame | NO | YES | 2 |  |  |  | This site may best be described as "If it 'aint broke, don't fix it" the booster pump draws water from the onsited storage tank and pummps into the onsite pressure vessel (currently controlled by pressure switch,) this can be priovided by utilizing PLC logic(I.E. Pressure sensor>I/O>BoosterPump.) The well that fills the storage tank is controlled by a warwick probe relay controller. I think too much effort would go into wiring new automation controlls for PLC logic when the solid state controls work. | 1
51 | Raymus Village waste Water | Wastewater Treatment | Wastewater-2 Pump flowmeter connection | [6 empty] | NO |  |  |  | NO-3 | YES |  | small fenced in site, there is room for an H frame west of transformer. In house improvements beig discussed with county engineers TBD |  | NO | 3 |  |  |  |  | 1
52 | Raymus Village Well #1 & #2 | Well | TCP Treatment plant -Tag read write | NO work needed , except D |  |  | ATI CL2 analyzer | IG41 I/O without PLC | ATI Chlorine Anylizer Modbus TCP-IP | NO |  |  |  | Existing, do not upgrade | YES |  | there is not enough room in panel, there is room for H frame adjacent to control cabinet see site photos for control equipment being installed | NO | NO | 1 |  |  |  | Monitor tags from AB Control Logix, alarm Control Logix Alarms, monitor system water pressure alarm high and low levels, monitor well motor current alarm high electrical current | 1
54 | Manteca Industrial Park County Service Area 30 Well #1 | Well | Well-1Pump Emergency Run |  | YES |  |  | IG41 I/O without PLC |  | NO |  |  |  | NO-3 | YES |  | there is room inside the building for h frame | NO | YES | 1 |  |  |  | monitor water pressure alarm for runtime (well is emergency use only notice to public must be issued within 24hrs upon runtime provide user defined setpoints to run and stop well pump motor | 1
55 | Manteca Industrial Park County Service Area 30 Well #2 | Well | Well-1Pump VFD |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | theris no room inside the building for h frame, there is room on the northern exposure for H frame | NO | YES | 1 |  |  |  | monitor and read modbus tags from Yaskawa drive, provide additional Water pressure sensor to monitored by PLC, alarm for low and high water pressure, alarm Yaskawa drive alarms | 1
56 | Rancho San Joaquin Maintenance District Well #1 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | no room in panel, would need a contrete footing for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
57 | Rancho San Joaquin Maintenance District Well #2 | Well | Well-1Pump VFD |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | see site photos, this is an outdoor facility and would need a secure enclosere adjacent to secure enclosure housing control cabinet | NO |  | 0 |  |  |  | monitor and read modbus tags from Yaskawa drive, alarm for low and high water pressure, alarm Yaskawa drive alarms | 3
58 | Elkhorn Estates Maintenance District Well #2 | Well | Well-1Pump |  | YES |  |  |  |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | no room in panel, outdoor site would need concrete footing H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 1
59 | Elkhorn Estates Maintenance District Well #1 | Well | Well-1Pump |  | YES |  |  | IG41 I/O without PLC |  | NO | pressure switch control requested |  |  | NO-3 | NO |  | no room in panel, room inside building for H frame | NO | YES | 1 |  |  |  | Monitor Water pressure, using user defined setpoints (within specified range) to provide I/O to call and stop well motor. monitor electrical current and alarm for low and high water pressure and high electrical current. | 2
60 | Bear Creek | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 |  |  | Outdoor facility, room to add H frame next to control cabinet | YES | NO | 2 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 4
61 | Blatt Estates CSA #46 | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Outdoor facility, room to add H frame next to control cabinet | YES | NO | 2 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 4
62 | Cherokee Industrial Park #1 CSA #17 | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | indoor facility room inside building for new equipment | YES | NO | 2 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 4
63 | Cherokee Industrial Park #2 CSA #17 | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | indoor facility has had a history of vandalism to the point the building is clad with 1/4" steel plate to deter break-ins.room inside building fo new cabinets | YES | NO | 2 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 4
64 | Terra Del Sol CSA #41 | Wastewater Treatment | Wastewater-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Outdoor facility, room to add H frame next to control cabinet | YES | NO | 2 |  |  |  | SJCoPW is looking into replacing the pump controller as the current controller is obsoletee and no longer supported more than likely add a level transducer and current transducers for alarms and monitoring | 2
65 | Lincoln Center Storm | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Small fenced in area | YES | NO | 1 |  |  |  | monitor storm sump level alarm for high and low levels, monitor and alarm current of storm pump motors | 4
66 | Forest Lake CSA #29 | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Room inside building to for new cabinet | YES | NO | 2 |  |  |  | Monitor storm sump level alarm for high and low levels, monitor and alarm current of storm pump motors, alert for power outage intrusion alarm and bypass, current pump controller is adequate | 2
67 | Lincoln Village Storm #1 | Storm Water | Storm-3Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Room inside building to for new cabinet |  | NO |  |  |  |  | new relay controlls installed in 2023, would perfer to utiilize them, use level transducer to monitor and report sump level, CT's on all motors to monitor runtime alarm for high level sump or transducer | 2
68 | Lincoln Village Storm #2 | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Room inside building to for new cabinet | YES | NO | 3 |  |  |  | new relay controlls installed in 2023, would perfer to utiilize them, use level transducer to monitor and report sump level, CT's on all motors to monitor runtime alarm for high level sump or transducer | 2
69 | Lincoln Village Storm #3 | Storm Water | Storm-3Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Room inside building to for new cabinet | YES | NO | 3 |  |  |  | new relay controlls installed in 2023, would perfer to utiilize them, use level transducer to monitor and report sump level, CT's on all motors to monitor runtime alarm for high level sump or transducer | 2
70 | Raymus Village Storm Site | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Room inside building to for new cabinet | YES | NO | 3 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 3
71 | Tallahatchey Terrace CSA #3 | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor site install H frame to north of control panel | YES | NO | 2 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 3
72 | Thornton Storm Site | Storm Water | Storm-3Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor site with a large control cabinet, if there is not room inside the cavbinet there is room on the northern exposure of control cabinet | YES | NO | 1 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 3
73 | Victor Storm Site | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Outdoor site Site has no shade, ecposed to the elements room to place H frame southeast of control panel | YES | NO | 3 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 3
74 | Morada Manor Storm | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Out door site, room available for H frame south of control cabinet and disconect cabinet | YES | NO | 1 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 4
75 | Morada Estates Zone A Storm Site | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor site with plenty of shade room for H frame next to control cabinet | YES | NO | 1 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 4
76 | Morada Estates North Storm Site | Storm Water | Storm-3Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor room north of control cabinet for H frame | YES | NO | 1 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 3
77 | Wilkinson Manor Storm Site | Storm Water | Storm-2Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor facility room adjacent for H frame | YES | NO | 3 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 3
78 | Oak Creek Storm Site | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor facility with adequate shade, room north of control cabinet for H frame | YES | NO | 2 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 4
79 | Lloyd Lane Storm Site #1 | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor facility in gated community adequate shade, room adjacent to control cabinet for H frame | YES | NO | 1 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 5
80 | Lloyd Lane Storm Site #2 | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | Out door facility, new h frame required best bet is to incorperate controls into new cabinet |  | NO | 1 |  |  |  | simple control cabinet is a small 8"x10" box housing HOA switch, circuit bresker, control relay attached to float switch, new PLC logic may be deployed, Level transducer to monitor sump level,current transducer, alarm high level sump, high electrical current | 4
81 | Lloyd Lane Storm Site #3 | Storm Water | Storm-1Pump |  | YES |  |  |  |  | NO |  |  |  | NO-3 | NO |  | outdoor facility shaded untill mid afternoon room for H frame adjacent to control cabinet | YES | NO | 1 |  |  |  | monitor sump level,motor current alarm high level sump high electrical current | 5
1